## Slide 1: INCREASED FIRE RESISTANCE OF A STEEL BEAM USING ORIENTED STANDARD BOARD CLADDING – A THERMAL ANALYSIS
Jakub Šejna
https://firesafetyengineering.net/

## Slide 2: Outline
Motivation
Introduction
Experiments
FE model
Summary

## Slide 3
Sustainability of structures - in case of fire
Reduction of CO2 emissions
Reduction of primary energy
Introduction
Experiments
FE model
Summary
Motivation
Unprotected steel member
Clading
wood-based cladding materials
Protected steel member
Primary energy
Wood : Cement = 1 : 3
Wood : Steel = 1 : 27
Wood : Aluminium = 1 : 70

## Slide 4
Design steel elements to their critical temperature
OK
What if the critical temperature is higher than 600 °C?
What if the design is badly dimensioned?
What If the steel temperatures are higher?
Introduction
Experiments
FE model
Summary
Unprotected steel element
Protected steel element
OSB cladding
Motivation
STEEL EN 1993-1-2
ok
?
ok
?
ok
?

## Slide 5
Introduction
Experiments
FE model
Summary
Introduction
TIMBER
STEEL
Comparison of procedures for additional fire protection proposals
Effect on mechanical analysis
EN 1993-1-2
EN 1995-1-2
Comparison
Experiment
+ FEM model

## Slide 6
Introduction
Experiments
FE model
Summary
Introduction
1974 Twild and Witteveen
35 mm softwood clading
+ 60 min of fire resistence of steel member
2019 Le
Timber–Steel Composites
Steel and mass timber
2020 Béreyziat
I or T steel profile
complete or partial fire protection by timber
2021 Bihina
Timber encasement of steel structures
alternative fire insulation
2021 Šalek
Numerical modelling
OSB cladding of wall
2022 Šejna and Šulc
Mechanical analysis
OSB cladding of steel beam
Pyrolysis of OSB
Development of char layer
Failure of cladding
Safe design:
Model of OSB burning as a fire protection material
doi: 10.1007/978-3-030-41235-7_58
doi:10.1002/cepa.1423
doi:10.1007/978-3-030-41235-7_58
doi: 10.14311/APP.2022.34.0116
doi: 10.3390/ma12234003

## Slide 7
Introduction
Experiments
FE model
Summary
Introduction
1974 Twild and Witteveen
35 mm softwood clading
+ 60 min of fire resistence of steel member
2019 Le
Timber–Steel Composites
Steel and mass timber
2020 Béreyziat
I or T steel profile
complete or partial fire protection by timber
2021 Bihina
Timber encasement of steel structures
alternative fire insulation
2021 Šalek
Numerical modelling
OSB cladding of wall
2022 Šejna and Šulc
Mechanical analysis
OSB cladding of steel beam
Pyrolysis of OSB
Development of char layer
Failure of cladding
Safe design:
Model of OSB burning as a fire protection material
doi: 10.1007/978-3-030-41235-7_58
doi:10.1002/cepa.1423
doi:10.1007/978-3-030-41235-7_58
doi: 10.14311/APP.2022.34.0116
doi: 10.3390/ma12234003

## Slide 8
Experiment
Horizontal furnace
Introduction
Experiments
FE model
Summary
5 samples
Unprotected beam, Length = 3.7 m, loaded
1x OSB protected beam, Length = 3.7 m, loaded
2x OSB protected beam, Length = 3.7 m, loaded
1x OSB protected beam, Length = 0.5 m, unloaded
2x OSB protected beam, Length = 0.5 m, unloaded
Location of elements based on the parametric study

## Slide 9
Horizontal furnace
Introduction
Experiments
FE model
Summary
Dimension 4.0 × 3.0 × 3.25 m
Experiment = 60 min
Temperature: Standard Temperature Curve
Ventilation = Automatic preasure 18 – 20 MPa
note: earlier experiments on the small scale
Samples
1x OSB = 1 × 22 mm OSB
2x OSB = 2 × 22 mm OSB
Thermocouples conducted in mineral insulation in the beam
Steel profile: SHS 100/6
Thermocouples: Under clading – on steel surface
MTC12 /1xK T2 /N4m /GHGH 2x0,5 / K-MM + MTC10 /1xK T2 /P1,5 /N3000 /K-MM

## Slide 10
2
1
3
4
5
6
7
8

## Slide 11
Experiment
1× OSB 22 mm
Introduction
Experiments
FE model
Summary
Load 0.982 kN
+ OSB 22mm → burn-off / fall-off in 20 min
60 min of experiment
temperature of steel = 868 °C maximum deflection unprotected beam no damage to the furnace

## Slide 12
2
1
3
6
5

## Slide 13
Experiment
TC placed under the OSB cladding on the surface of steel
Introduction
Experiments
FE model
Summary
Time [min] | Temperature in furnace [°C] | Unprotected beam (reference) [°C] | 1× OSB 22 mm protected beam TC 18 [°C]
15 | 747 | 632 | 94
30 | 848 | 816 | 371
45 | 902 | 921 | 860
60 | 948 | 940 | 868
Temperatures

## Slide 14
Introduction
Experiments
FE model
Summary
Time [min] | Temperature in furnace [°C] | Unprotected beam (reference) [mm] | 1× OSB 22 mm protected beam [mm]
15 | 747 | 26 | 0
30 | 848 | 211 | 36
45 | 902 | 278 | 173
60 | 948 | 648 | 251
Displacement

## Slide 15
FE Model
ANSYS Mechanical
Sensitivity analysis
Tested on 2D cross-section
solved following already performed temperature analysis
MESH taken over for mechanical analysis
Calculation time considered
Temperature analysis = 15 days
Mechanical analysis = 3 days
Introduction
Experiments
FEM model
Summary
INSULATED
INSULATED
1 kN
1 mm space in cladding
MINERAL WOOL STEEL OSB CLADDING
AIR
for one calculation
AMD Ryzen 7 3750H with Radeon Vega Mobile Gfx 2.30 GHz, RAM 24 GB

## Slide 17
FE Model
ANSYS Mechanical – Thermal analysis
Version 2021
Material properties EN 1993-1-2 EN 1995-1-2
implicit analysis
Introduction
Experiments
FE model
Summary
MESH | No.1 | No.2 | No.3 | No.4
Nodes | 42861 | 2269313 | 50772 | 41946889
Elements | 7410 | 489949 | 25130 | 30111563
Type of MESH | hexagonal | hexagonal | tetrahedrons | hybrid-tetrahedrons
Calculation time | 1 day | 17 days | 3 days | 23 days
AMD Ryzen 7 3750H with Radeon Vega Mobile Gfx 2.30 GHz, RAM 24 GB
Developing of a model for cladding failure
Temperatures applied to the surface from the experiment emissivity of OSB = 0.80 convection factor = 25 kW/m2

## Slide 18
Vojta Šálek
CFD model
With pyrolysis
Jakub Šejna
FE model

## Slide 19
FE model
FE model
CFD model
CFD model

## Slide 20
OLD
NEW
MESH | No.4
Nodes | 41 946 889
Elements | 30 111 563
Type of MESH | hybrid-tetrahedrons
Calculation time | 23 days
MESH | No.4
Nodes | 130 271 000
Elements | 93 720 140
Type of MESH | hybrid-tetrahedrons
Calculation time | 2 days
AMD Ryzen 7 3750H with Radeon Vega Mobile Gfx 2.30 GHz,
socket: 4; processor: 8;, RAM 24 GB
Intel(R) Xeon(R) Gold 6144 CPU @3.50 GHz; socket: 16; virtual processor: 32; RAM 20 GB

## Slide 21
Introduction
Experiments
FE model
Summary
45 °C
3 °C

## Slide 22
Introduction
Experiments
FE model
Summary
0 s
100 s
200 s
400 s
800 s
1600 s

## Slide 23
Developing a model with OSB cladding failure simulation
Combining knowledge from FE models and CFD models with pyrolysis
Introduction
Experiments
FE model
Summary

## Slide 24: Summary
Despite the need to refine the development of the density of the OSB cladding for modelling (dependent on temperature)
Considering the failure time of the cladding, and the correct design of the OSB cladding thickness, the fire resistance of the steel beam can be increased by up to 30 minutes, for single-layer cladding – 22 mm.
Introduction
Experiments
FE model
Summary

## Slide 25: THANK YOU FOR ATTENTION
JAKUB ŠEJNA